Sun-Day Corporation

8330 Manchester Road

St. Louis, MO  63144

(P) 314/961-0197  (F) 314/961-6336

hbush@sun-day.com

# Sentry Leak Detection System

NEMA 4X thermoplastic enclosure with liquid

leak detection sensor (Polypropylene optical),

alarm horn, push button/alarm silence with

light and power on light.

Unit operates on 120VAC power.

Installation		Trouble Shooting

1) Mount Leak Detection Panel in area near the tank.		* I hooked up the 120VAC line and there is no power

25’ length of the sensor cable as a standard, but this	to the unit when I turn the Power ON switch.

can be lengthened.

  Check to see that there is a fuse in the fuse

2) Bring 120VAC Power to panel and make connections	holder, that the fuse holder is closed, that the  to appropriate terminals (L1, Neutral & Ground).		fuse has not blown.

3) Connect the sensor to the appropriate terminals on the 	* I have power to the unit, Power light is ON but the

power strip. Turn on the power to the panel. Place the  	the Leak Detection Alarm will not sound.

sensor in a cup filled with water, this will sound the

alarm horn. Press the silence button to stop the horn;	  Check to see that the Leak Detection Sensor

the pilot light will remain on. Remove the sensor from	wires are properly connected & secure.

the water; this will cause the alarm pilot light to turn   	(See supplied drawing)

off and will reset the latching relay. If the test performs 	  Check to see that the sensor is installed

as designed, proceed to the next section.		correctly. (See #4 under Installation section)

4) Mounting of the Leak Detection sensor. Lower the  	* How do I check that the sensor is working?

sensor through the supplied fitting, on the tank sidewall,

down the interstitial space (area between the inner &   	  Remove the sensor from the tank and place the

outer tanks) until the sensor reaches the bottom of the 	end of the sensor in a cup filled with water.

secondary containment tank. After the sensor has 	 	This should sound the alarm horn.

reached bottom, pull the sensor back up so that it is 	Should the alarm not sound replace the sensor.

now just off the bottom of the secondary containment

tank (approximately 1/2").

5) Verify that all connections are made correctly & secure.

Turn the power on to the panel.